## Network_Drawing
[16 empty] | mn |  | no |  | Unit Name | Unit Type | Feed Stream | Product Stream | Waste Stream | Stream Name | Source | Dest
[15 empty] | M |  |  |  |  | A | Feed |  | ac |  | ac | A | C
A |  |  |  | S |  |  | U | [8 empty] | lm | N |  | O | B | Feed |  | bc |  | bc | B | C
[20 empty] | C | Mixer | ac,bc | cd |  | cd | C | D
[6 empty] | fu | [8 empty] | L | lv |  |  |  | D | SF | cd | de | ds | de | D | E
|  |  | ds | [13 empty] | V |  |  | E | Lamella | de | ef | et | ef | E | F
ac | C |  | D | E |  | F |  | G |  | H |  | I |  | J | K | kl |  |  |  | F | MMF | ef | fg | fu | fg | F | G
|  | cd | de |  | ef |  | fg |  | gh |  | hi |  | ij |  | jk |  |  |  |  | G | CF | fg | gh |  | gh | G | H
[20 empty] | H | Hydrated Lime | gh | hi |  | hi | H | I
[16 empty] | kp |  |  |  | I | Limestone | hi | ij |  | ij | I | J
bc |  |  |  | et | [15 empty] | J | IX | ij | jk |  | jk | J | K
[20 empty] | K | RO | jk | kl | kp | kl | K | L
[15 empty] | P |  |  |  |  | L | EDI | kl | lm | lv | kp | K | P
[5 empty] | T | [14 empty] | M | O2 | lm | mn |  | lm | L | M
B | [17 empty] | R |  | N | CO2 | mn | no |  | mn | M | N
[16 empty] | pr |  |  |  | O | ProductOut | no |  |  | no | N | O
[15 empty] | pq |  |  |  |  | P | Splitter | kp | pq,pr |  | pq | P | Q
[20 empty] | Q | WasteOut | pq |  |  | pr | P | R
[20 empty] | R | WasteOut | pr |  |  | ds | D | S
[15 empty] | Q |  |  |  |  | S | WasteOut | ds |  |  | fu | F | U
[20 empty] | T | WasteOut | et |  |  | et | E | T
[20 empty] | U | WasteOut | fu |  |  | lv | L | V
[20 empty] | V | WasteOut | lv
Feed
SF
Lamella
MMF
CF
HydratedLime
LimeStone
IX
RO
WasteOut
Mixer
WasteOut
WasteOut
Feed
EDI
O2
CO2
ProductOut
S
WasteOut
WasteOut
WasteOut

## Network_Info
[12 empty] | Volume Flow | Temperature | Pressure | IonicCon | Length | Area | Volume | Flux | Mass Flow | Density | Viscosity | HeatCapacity | LatentHeat | Voltage | Current | Resistivity | Conductivity | AC Power | DC Power | AC Energy | Time | Mass
Unit Name | Unit Type | Feed Stream | Product Stream | Waste Stream | Stream Name | Source | Dest | Solve Order | Tear Stream | Source Node | Source Stream | cum/hr | C | bar | ppm | m | sqm | cum | gal/sqft-min | kg/hr | kg/cum | cP | kJ/kg C | kJ/kg | Volts | Amp | MOhm-cm | uS/cm | kWhr | kW | kWhr/1000gal | min | kg
A | Feed |  | ac |  | ac | A | C | B |  | A | ac
B | Feed |  | bc |  | bc | B | C | A |  | B | bc
C | Mixer | ac,bc | cd |  | cd | C | D | C
D | SF | cd | de | ds | de | D | E | D
E | Lamella | de | ef | et | ef | E | F | E
F | MMF | ef | fg | fu | fg | F | G | T
G | CF | fg | gh |  | gh | G | H | F
H | Hydrated Lime | gh | hi |  | hi | H | I | G
I | Limestone | hi | ij |  | ij | I | J | H
J | IXMB | ij | jk |  | jk | J | K | I
K | RO | jk | kl | kp | kl | K | L | J
L | EDI | kl | lm | lv | kp | K | P | K
M | O2 | lm | mn |  | lm | L | M | P
N | CO2 | mn | no |  | mn | M | N | R
O | ProductOut | no |  |  | no | N | O | Q
P | Splitter | kp | pq,pr |  | pq | P | Q | L
Q | WasteOut | pq |  |  | pr | P | R | V
R | WasteOut | pr |  |  | ds | D | S | M
S | WasteOut | ds |  |  | fu | F | U | N
T | WasteOut | et |  |  | et | E | T | O
U | WasteOut | fu |  |  | lv | L | V | U
V | WasteOut | lv | [5 empty] | S
DC Power
AC Energy
Time

## unitop_input
unitop Name | name | A | unitop Name | name | B | unitop Name | name | C | unitop Name | name | D | unitop Name | name | E | unitop Name | name | F | unitop Name | name | G | unitop Name | name | H | unitop Name | name | I | unitop Name | name | J | unitop Name | name | K | unitop Name | name | L |  | unitop Name | name | M | unitop Name | name | N | unitop Name | name | O | unitop Name | name | P | unitop Name | name | Q | unitop Name | name | R | unitop Name | name | S | unitop Name | name | T | unitop Name | name | U | unitop Name | name | V
Unitop Type | unitop | Feed | Unitop Type | unitop | Feed | Unitop Type | unitop | Mixer | Unitop Type | unitop | SF | Unitop Type | unitop | Lamella | Unitop Type | unitop | MMF | Unitop Type | unitop | CF | Unitop Type | unitop | HydratedLime | Unitop Type | unitop | LimeStone | Unitop Type | unitop | IXMB | Unitop Type | unitop | RO | Unitop Type | unitop | EDI |  | Unitop Type | unitop | O2 | Unitop Type | unitop | CO2 | Unitop Type | unitop | ProductOut | Unitop Type | unitop | Splitter | Unitop Type | unitop | WasteOut | Unitop Type | unitop | WasteOut | Unitop Type | unitop | WasteOut | Unitop Type | unitop | WasteOut | Unitop Type | unitop | WasteOut | Unitop Type | unitop | WasteOut
Feed Stream | feed |  | Feed Stream | feed |  | Feed Stream | feed | ac,bc | Feed Stream | feed | cd | Feed Stream | feed | de | Feed Stream | feed | ef | Feed Stream | feed | fg | Feed Stream | feed | gh | Feed Stream | feed | hi | Feed Stream | feed | ij | Feed Stream | feed | jk | Feed Stream | feed | kl |  | Feed Stream | feed | lm | Feed Stream | feed | mn | Feed Stream | feed | no | Feed Stream | feed | kp | Feed Stream | feed | pq | Feed Stream | feed | pr | Feed Stream | feed | ds | Feed Stream | feed | et | Feed Stream | feed | fu | Feed Stream | feed | lv
Product Stream | product | ac | Product Stream | product | bc | Product Stream | product | cd | Product Stream | product | de | Product Stream | product | ef | Product Stream | product | fg | Product Stream | product | gh | Product Stream | product | hi | Product Stream | product | ij | Product Stream | product | jk | Product Stream | product | kl | Product Stream | product | lm |  | Product Stream | product | mn | Product Stream | product | no |  |  |  | Product Stream | product | pq,pr
Waste Stream | waste |  | Waste Stream | waste |  | Waste Stream | waste |  | Waste Stream | waste | ds | Waste Stream | waste | et | Waste Stream | waste | fu | Waste Stream | waste |  | Waste Stream | waste |  | Waste Stream | waste |  | Waste Stream | waste |  | Waste Stream | waste | kp | Waste Stream | waste | lv |  | Waste Stream | waste |  | Waste Stream | waste |  |  |  |  | Waste Stream | waste
Flow | flow | 10 | Flow | flow | 90 |  |  |  | Application | application | Non-MBR | Clarifier Sludge Blowdown | clarifier_sludge_blowdown | 1.5 | Filter Type | filter_type | Vertical Multimedia Filter | Filter Type | filter_type | RO.Zs 05-40 | CO2 add | co2_add | 20 | Remineralization Bypass | remin_bypass | 10 | Cation | cation_res | PFC-100 H | System Recovery | recovery_stg1 | 75 | Model Type | model_type | MK-3 |  | Tower Diameter | tower_diameter | 2.4384 | Normal Flow Rate | flow_rate_norm | 227.1246 |  |  |  | Split Fraction | pq | 0.9
Temperature | temp | 25 | Temperature | temp | 25 |  |  |  | Feed Water | fwtype | Surface Water | Chemical Selection | chemical_selection | Al2(SO4)3 | Total Design Flow rate | tot_design_flow | 227.1246 | Flow per TIE | flow_per_tie | 0.91 | Ca(OH)2 | caoh2 | 10 | Reactive CO2/H2SO4 | reactive_co2_by_h2so4 | 85 | Anion | anion_res | PFA-400 Cl | Element Type | element_type | BWRO | Co- Current Flow | co_current | 0 |  | Inlet O2 Stage 1 | o2_in_stage1 | 10 | CO2 Concentration Out | co2_out | 5 |  |  |  | split Fraction | pr | 0.1
Pressure | press | 1 | Pressure | press | 1 |  |  |  | Recovery | recovery | 90 | Kg dry sludge/kg Al2(SO4)3 coagulant | dry_sludge_per_chemical_dosage | 44 | Total Maximum Flow rate | tot_max_flow | 227.1246 |  |  |  | NaOH | naoh | 9.1 | CO2 Stream 1A | co2_add_1a | 15 | Inert | inert_res | No | Elements per vessel | elementspervessel | 6 | RO permeate softening | ro_perm_soft | 0 |  | Inlet N2 Stage 1 | n2_in_stage1 | 17 | Liquid Loading Rate | liq_load | 36
Calcium | ca | 100 | Calcium | ca | 1000 | [6 empty] | % of Sludge as fixed soils | sludge_fixed_soils | 95 | Total number of installed unit(s), Optional | tot_units | 1 | [6 empty] | CO2 Stream 1B | co2_add_1b | 12 | SAC Unit Leakage | sac_unit_leakage | 1 | Average Flux | avg_flux_stg1 | 0.0083333 | 3X-HH Stack | hhard | 1 |  | Inlet CO2 Stage 1 | co2_in_stage1 | 0 | a | a | 26.92
Magnesium | mg | 90 | Magnesium | mg | 100 | [6 empty] | Fixed Soil Specific Gravity | fixed_soil_sg | 2.5 | Unit(s) in service, normally (Optional) | service_units | 1 | [6 empty] | NaOH | naoh | 12 | SBA Unit Leakage | sba_unit_leakage | 0.1 | Element Area | membrane_area | 37.158 | Target Resistivity | target_resistivity | 16 |  | Outlet O2 Stage 2 | o2_out_stage2 | 0.007 | b | b | -0.61
Sodium | na | 80 | Sodium | na | 444.42 | [6 empty] | Volatile Soil Specific Gravity | volatile_soil_sg | 1 | Inlet Total Suspended Solids, Optional | inlet_tss | 10 | [6 empty] | H2SO4 | h2so4 | 200 | Cation Exchange Capacity | sac_kgr_per_ft3 | 10 | Element Age | element_age | 1 | Flow per stack | flowperstack | 3.41 | 9.08 | Stage-1 Tower Packing Depth | pack_depth_stage_1 | 3.048 | c | c | 0.029
Potassium | k | 85 | Potassium | k | 10 | [6 empty] | Clarifier Diameter | clarifier_dia | 12.5 | Inlet Total Organic Carbon, Optional | inlet_toc | 5 | [6 empty] | Remineralization Type | remin_type | gravity | Anion Exchange Capacity | sba_kgr_per_ft3 | 10 | Flux Annual percent change | flux_change | 5 | Target Silica | target_silica | 20 |  | Stage-1 Inlet to Packing Height | inlet_to_packheight | 1.3716 | d | d | -0.0008
Ammonia | nh4 | 70 | Ammonia | nh4 | 0 | [6 empty] | Clarifier Active Depth | clarifier_active_depth | 3.7 | Inlet Chlorine, Optional | inlet_chlorine | 0.5 | [6 empty] | Reactor Length | reactor_length | 12.9 | Acid Dosage | acid_dosage | 128.1476 | Salt passage Annual percent change | saltpassage_change | 7 | Rectifier efficiency | rect_eff | 70 |  | Stage-1 Inlet to Upper Head T.L. | inlet_to_upperhead | 0.2286 | e | e | 8e-06
Barium | ba | 60 | Barium | ba | 0.01 | [6 empty] | Clarifier Flocculation Zone Area to total Area (%) | clarifier_flocculation_area_to_total_area | 20 | Media Bed Freeboard | free_board | 50 | [6 empty] | Reactor Width | reactor_width | 6 | Caustic Dosage | caustic_dosage | 128.1476 | Pump Efficiency | pump_eff | 84 | Recifier DC output | rect_dc_volt | 400 |  | Stage-2 Tower Packing Depth | pack_depth_stage_2 | 3.048 | Clearwell Retention Time | ret_time | 3
Strontium | sr | 65 | Strontium | sr | 0.1 | [9 empty] | Back wash Temp, High | bw_temp_high | 32.2222 | [6 empty] | Assumed Bed depth | bed_depth_assumed | 2 | acid_type | acid_type | H2SO4 | Ca | ca_rej | 99 | Feed Pressure | feed_pressure | 4.1368 |  | Stage-2 Loop Seal Height | loop_seal_height | 1.2192 | Turndown Ratio | turndown_ratio | 5
Iron | fe | 55 | Iron | fe | 1 | [9 empty] | Back wash Temp, Low | bw_temp_low | 5.5556 | [6 empty] | Reduction in Finshed bed depth | finished_bed_depth_reduction | 0.95 | Acid Concetration | acid_concetration | 93 | Mg | mg_rej | 99.1 |  |  |  |  | Clearwell Retention Time | ret_time | 3 | Tower Height | tow_height | 3.048
Maganese | mn | 50 | Maganese | mn | 0 | [9 empty] | Post back wash rinse | post_bw_rinse | Yes | [6 empty] | Number of Spare Units (N + ) | no_spare_units | 2 | Acid Step 1 | acid_step_1 | 2 | Na | na_rej | 98.8 |  |  |  |  | Clearwell Straight Side Height | clearwell_straight_height | 6.096 | Clearwell Height | clear_height | 4.572
Copper | cu | 20 | Copper | cu | 0 | [9 empty] | Air Scour | airscour | No | [6 empty] | Assumed CaCO3 purity | caco3_purity | 0.99 | Acid Step 2 | acid_step_2 | 4 | K | k_rej | 98.2 |  |  |  |  | Pump Outlet Diameter | pump_out_dia | 0.3048 | Packing Support Grating Height | pack_supp_grat_height | 0.0381
Aluminium | al | 10 | Aluminium | al | 0 | [9 empty] | Sub surface wash | ssw | Yes | [6 empty] | Assumed CaCO3 specific gravity | caco3_sg | 1450 | Dilute Caustic | dilute_caustic | 4 | NH4 | nh4_rej | 81 |  |  |  |  | Low-Low Level alarm | lll_alarm | 0.0762 | Overflow Nozzle Diameter | overflow_nozz_dia | 0.3048
Sulfate | so4 | 200 | Sulfate | so4 | 500 | [9 empty] | Design Pressure | design_pressure | 10.3421 | [9 empty] | Concentric Caustic | conc_caustic | 50 | Ba | ba_rej | 99 |  |  |  |  | Low Level alarm | ll_alarm | 0.0762 | Inlet Header Distributor Size | inlet_header_size | 0.254
Chloride | cl | 150 | Chloride | cl | 2300 | [9 empty] | Corrosion allowance (Optional) | corr_allowance | 0 | [9 empty] | Normal Flow Rate | normal_flow_rate | 11.3562 | Sr | sr_rej | 99 |  |  |  |  | High Level alarm | hl_alarm | 0.0762 | Spray Nozzle Height | spray_nozzle_height | 0.14986
Fluoride | f | 155 | Fluoride | f | 0.1 | [9 empty] | Choice of lining | lining_type | Plasite | [9 empty] | Run Length | run_length | 1439.9971 | Fe | fe_rej | 99 |  |  |  |  | Inlet Diameter | inlet_dia | 0.254 | Fan Size | fan_size | 3
Nitrate | no3 | 110 | Nitrate | no3 | 1 | [9 empty] | Outer Diameter | outer_dia | 3.6576 | [9 empty] | Use gross flow as serviceflow | use_gross_flow_as_serviceflow | No | Mn | mn_rej | 0 |  |  |  |  | Overflow | overflow | 0.4572
Bromide | br | 35 | Bromide | br | 0 | [9 empty] | Tan length | tan_length | 10.9728 | [9 empty] | Recycle Mixed Bed | recycle_mixed_bed | No | SO4 | so4_rej | 99 |  |  |  |  | Skirt Straight Side Height | skirt_straight_height | 6.096
Phosphate | po4 | 25 | Phosphate | po4 | 5 | [9 empty] | Head Type | head_type | ASME F&D | [9 empty] | Inert Resins | inert_resins | No | Cl | cl_rej | 98.9
Boron | b | 15 | Boron | b | 0 | [9 empty] | Sand Depth | sand_depth | 0.3048 | [9 empty] | Ambersep Resins | ambersep_resins | No | F | f_rej | 99.8
Silica | sio2 | 5 | Silica | sio2 | 50 | [9 empty] | Anthracite Depth | anthracite_depth | 0.4572 | [9 empty] | Backwash Source | backwash_source | Influent | NO3 | no3_rej | 93
Hydrogen Sulfide | h2s | 75 | Hydrogen Sulfide | h2s | 0 | [9 empty] | Garnet Depth | garnet_depth | 0.2286 | [9 empty] | Heated Caustic | heated_caustic | Yes | Br | br_rej | 98.8
Bicarbonate | hco3 | 85 | Bicarbonate | hco3 | 146.05 | [9 empty] | Sub Fill Type | subfill_type | Carbon | [9 empty] | Underdrain Type | underdrain_type | Flat Strainer Plate | PO4 | po4_rej | 99
Carbon Dioxide | co2 | 115 | Carbon Dioxide | co2 | 18.22 | [9 empty] | Green Sand Load | greensand_load | 0 | [9 empty] | Lining Thickness | lining_thickness | 0.0047625 | B | b_rej | 50
Carbonate | co3 | 125 | Carbonate | co3 | 0.19 | [9 empty] | Anthracite Cap | anthracite_cap | Yes | [9 empty] | force bed depth cation | force_bed_depth_cation | 10 | Silica | sio2_rej | 98
TSS | tss | 135 | TSS | tss | 135 | [9 empty] | Loading Rate | loading_rate | 2 | [9 empty] | force bed depth anion | force_bed_depth_anion | 10 | H2S | h2s_rej | 1
TOC | toc | 145 | TOC | toc | 145 | [9 empty] | Shell Joint efficiency | shelljoint_eff | 0.85 | [9 empty] | MB Diameter | mb_diameter | 0.9144 | HCO3 | hco3_rej | 98.4
DOC | doc | 205 | DOC | doc | 205 | [9 empty] | Head Joint efficiency | headjoint_eff | 1 | [9 empty] | MB Freeboard | mb_freeboard | 100 | CO2 | co2_rej | 2
TKN | tkn | 95 | TKN | tkn | 95 | [9 empty] | Backwash Time | backwash_time | [10 empty] | Design Pressure | design_pressure | 100 | CO3 | co3_rej | 99.9
COD | cod | 165 | COD | cod | 165 | [9 empty] | Drain Time | drain_time | [10 empty] | Resin high temperature | resin_high_temperature | 29.4444
Turbidity | turbidity | 175 | Turbidity | turbidity | 175 | [9 empty] | Refill Time | refill_time | [10 empty] | Regen Temperature | regen_temperature | 48.8889
Color | color | 7 | Color | color | 7 | [9 empty] | Rinse Time | rinse_time | [10 empty] | a | a | 1.2345
M-Alkalinity | malk | 225 | M-Alkalinity | malk | 120 | [9 empty] | Subsurface Wash Time | ssw_time | [10 empty] | b | b | 0.026088
pH | ph | 8 | pH | ph | 7 | [9 empty] | Whether rinse flow is same as service flow? | rinse_serviceflow | No | [9 empty] | c | c | 0.000141
[15 empty] | Whether rinse flow is recycled? | rinse_feed | Yes | [9 empty] | d | d | -1.79e-08
[15 empty] | Drain Time (Optional) | drain_time | [10 empty] | Slow BW [w/ classify] % | slow_with_classify | 65
[15 empty] | Refill Time (Optional) | refill_time | [10 empty] | Slow [w/o classify] & Classify BW % | slow_without_classify_and_classify_backwash | 50
[15 empty] | Rinse Time (Optional) | rinse_time | [10 empty] | Acid injection flow | acid_injection_flow_rate_per_volume | 0.686
[15 empty] | Subsurface Wash Time (Optional) | ssw_time | [10 empty] | Caustic injection flow | caustic_injection_flow_rate_per_volume | 0.383
[15 empty] | Rinse flow to be maintained same as service flow | rinse_serviceflow | Yes/No | [9 empty] | Use service flow for rinse ? | use_service_flow_for_rinse | Yes
[15 empty] | Rinse water recycled to feed | rinse_feed | Yes/No

## unitop_output
Unitop Name | A | Unitop Name | B | Unitop Name | C | Unitop Name | D | Unitop Name | Lamella1 | Unitop Name | MF1 | Unitop Name | CF1 | Unitop Name | Hydratedlime1 | Unitop Name | Limestone1 | Unitop Name | MB1 | Unitop Name | RO1 | Unitop Name | EDI1 | Unitop Name | O21 | Unitop Name | CO21 | Unitop Type | ProductOut | Unitop Name | P | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut
Unitop Type | Feed | Unitop Type | Feed | Unitop Type | Mixer | Unitop Type | SF | Unitop Type | Lamella | Unitop Type | MF | Unitop Type | CF | Unitop Type | Hydratedlime | Unitop Type | Limestone | Unitop Type | MB | Unitop Type | RO | Unitop Type | EDI | Unitop Type | O2 | Unitop Type | CO2 | Unitop Name | O | Unitop Type | Splitter | Unitop Name | Q | Unitop Name | R | Unitop Name | S | Unitop Name | T | Unitop Name | U | Unitop Name | V
Bicarbonate | 116.6691 | Bicarbonate | 144.2517 |  |  | Maximum screen opening size | 500 micron | RW Clarifier Feed Flowrate | 90 | Diameter | 3.6576 | Total Feed Flow Rate | 87.0092 | Flow Rate | 87.0092 | Flow Rate | 87.0092 | Diameter | 0.9144 | Feed Flow Rate | 87.0092 | Product Flow Rate | 65.257 | Flow Rate | 65.2571 | Tower Diameter | 1.2192
Carbonate | 0.92015 | Carbonate | 0.14305 |  |  |  |  | Clarifier Product Flow Rate | 89.271 | Straight Shell Height | 1.6764 | No: of Filters | 24 | Temperature | 87.0092 | Temperature | 25 | Straight Shell Height | 40.2336 | Permeate Flow Rate | 65.2569 | Product Resistivity | 0 | Flux | 5.716 | Tower Height | 3.048
Co2 | 1.497 | Co2 | 15.9311 |  |  |  |  | RW Clarifier Blowdown Flowrate | 0.72905 | Vessel Design Pressure | 10.4365 | Filter DP | 0.07438 | Na | 25 | Na | 470.6782 | Vessel Design Pressure | 100.0946 | Concentrate Flow Rate | 21.7523 | Product Silica guarantee level | 0 | Inlet O2 Stage 1 | 10 | Clearwell Diameter | 1.2192
TDS | 1698.1835 | TDS | 4571.963 |  |  |  |  | Dosage | 10.0847 | Vessel Test Pressure | 13.5371 | Actual Flow per TIE | 0.90635 | K | 405.1783 | K | 8.9993 | Cation | PFC-100 H | Feed TDS | 4678.784 | Predicted Silica product | 0 | Inlet N2 Stage 1 | 17 | Clearwell Height | 4.572
[8 empty] | Hydraulic Surface Loading Rate-Based on Product Flow Rate | 0.37174 | Volume of Anthracite/Unit | 4.7125 |  |  | Ca | 8.9993 | Ca | 992.368 | Anion | PFA-400 Cl | Permeate TDS | 55.0814 | Predicted Max product sodium | 0 | Outlet O2 Stage 1 | 0.26458 | Tower + Clearwell Height | 7.62
[8 empty] | Hydraulic Surface Loading Rate-Based on Feed Flow Rate | 0.37477 | Anthracite bed depth | 0.4572 |  |  | Mg | 905.333 | Mg | 89.9928 | Inert | N/A | Concentrate TDS | 18550.8478 | Predicted Max product chloride | 0 | Outlet N2 Stage 1 | 0.23132 | Overall Height [indoors] | 7.7724
[8 empty] | Clarifier Diameter | 12.5 | Volume of Filter sand /Unit | 3.1417 |  |  | HCO3 | 89.9928 | HCO3 | 364.9345 | Cation Resin Volume / Unit | 5.3802 | Feed Pressure | 12.0225 | Predicted Max product sulfate | 0 | Outlet O2 Stage 2 | 0.007 | Overall Height [outdoors] | 8.0772
[8 empty] | Clarifier Flocculation Zone Area to total Area (%) | 20 | Filter sand bed depth | 0.3048 |  |  | CO3 | 160.4378 | CO3 | 3.8293 | Anion Resin Volume / Unit | 5.3802 | Pressure Vessels | 15 | Maximum Allowable Recovery | 0 | Outlet N2 Stage 2 | 0.0031477 | Packing Volume | 2.8317
[8 empty] | Clarifier Active Depth | 3.7 | Volume of Garnet/Unit | 2.3563 |  |  | CO2 | 0.056847 | CO2 | 3.8076 | Inert Resin Volume / Unit | 0 | Total Elements | 87 | No: of E-cell Stacks | 0 | NCG Load Stage 1 | 1.8393 | Packing Depth | 2.413
[8 empty] | Flocculation Zone HRT | 60.5352 | Garnet bed depth | 0.2286 |  |  | Cl | 49.2845 | Cl | 2070.2068 | Resin Bed Depth - Total | 20.105 |  |  | Current | 0 | H2O Load Stage 1 | 1.7741 | Design Flow | 65.2571
[8 empty] | Total HRT | 302.6759 | Volume of Greensand/Unit |  |  |  | SO4 | 2070.2068 | SO4 | 626.2903 | Cation Dosage - 100% h2so4 | 128.148 |  |  | Voltage | 0 | Volume Flow Stage 1 | 90.7807 | Normal Flow | 227.125
[8 empty] | Flocculator Cylinder Diameter | 5.5916 | Greensand bed depth |  |  |  | B | 449.9638 | B | 0 | Anion Dosage - 100% NaOH | 128.148 |  |  | DC power | 0 | Vacuum Stage 1 | 0.04945 | Design Flux | 22.9
[10 empty] | Volume of Carbon/Unit |  |  |  | Hardness | 0 | Hardness | 2851.6903 | Cation Exchange Capacity | 10 |  |  | AC power consumption | 0 | NCG Load Stage 2 | 0.12923 | Normal Flux | 79.6
[10 empty] | Carbon bed depth |  |  |  | pH | 2634.1027 | pH | 8.0252 | Anion Exchange Capacity | 10 |  |  | AC energy | 0 | H2O Load Stage 2 | 3.2417 | Clearwell Usable Capacity | 4.41
[10 empty] | Subfill Volume [to top of underdrain] | 3.8843 |  |  | Alkalinity | 6.5636 | Alkalinity | 308.5802 | Design Flow Rate | 87.0094 |  |  | Feed pressure | 0 | Volume Flow Stage 2 | 165.8779 | Clearwell Usable Depth | 3.7846
[10 empty] | Maximum Service Flow Rate per unit | 227.125 |  |  | LSI | 132.3647 | LSI | 1.9317 | Normal Flow Rate | 87.0094 |  |  | Predicted Product outlet pressure | 0 | Vacuum Stage 2 | 0.030833 | Influent CO2 ppm as CaCO3 | 4
[10 empty] | Design Service Flow Rate per unit | 227.125 |  |  | CO2 addition | 0.064371 | Remineralization Bypass | 10 | Run Time Between Regenerations at Design Flow Rate | 1440 |  |  | Feed Inlet | 65.257 | Tower Diameter | 2.4384 | Influent CO2 ppm as CO2 | 3.5
[10 empty] | Maximum Flux Rate | 9.0132 |  |  | Ca(OH)2 addition | 20 | Reactive CO2/H2SO4 | 85 | Run Time Between Regenerations at Normal Flow Rate | 1440 |  |  | Concentrate Bleed | 0 | Clearwell Diameter | 2.4384 | Effluent CO2 ppm as CaCO3 | 5
[10 empty] | Design Flux Rate | 9.0132 |  |  | NaOH addition | 10 | CO2 Stream 1A | 15 | Gross Throughput | 134072.331 |  |  | Electrode Bleed | 0 | Clearwell Volume | 23.725 | Effluent CO2 ppm as CO2 | 4.4
[10 empty] | Max Flow Rate/Media Volume | 4.0059 |  |  | CO2 Flow Rate | 9.1 | CO2 Stream 1B | 12 | Net Throughput | 125293.4955 |  |  |  |  | Straight Side Height Excluding Skirt | 15.0114 | Design [Minimum] Water Temperature | 25
[10 empty] | Design Flow Rate/Media Volume | 4.0059 |  |  | Ca(OH)2 Flow Rate | 1.7402 | NaOH | 12 | Cation Influent Load | 3893.6049 |  |  |  |  | Straight Side Height Including Skirt | 21.1074 | Recommended Fan Size | 1464.4696
[10 empty] | System Recovery | 97.4662 |  |  | NaOH Flow Rate | 0.87009 | H2SO4 | 200 | Anion Influent Load | 3926.4589 |  |  |  |  | Stage-1 Tower Packing Depth | 3.048 | Fan Size per Flow Rate | 3
[10 empty] | Draindown Flow | 0 |  |  |  |  | CaCO3 Consumption | 241.764 | Cation Exchange Capacity / Regeneration | 1900 |  |  |  |  | Stage-2 Tower Packing Depth | 3.048
[10 empty] | Draindown Time | 0 |  |  |  |  | CO2 Stream 1A Flow Rate | 0.13051 | Anion Exchange Capacity / Regeneration | 1900
[10 empty] | Draindown Volume | 0 |  |  |  |  | CO2 Stream 1B Flow Rate | 0.9397 | Design Flux Rate | 66.4978
[10 empty] | Air Scour Flow | 0 |  |  |  |  | NaOH Flow Rate | 1.0441 | Normal Flux Rate | 66.4978
[10 empty] | Air Scour Time | 0 |  |  |  |  | H2SO4 Flow Rate | 15.6617 | Design Flowrate / Resin Volume | 1.0081
[10 empty] | Refill Flow | 0 |  |  |  |  | CaCO3 Consumption Flow Rate | 18.9321 | Normal Flowrate / Resin Volume | 1.0081
[10 empty] | Refill Time | 0 |  |  |  |  | Remineralization Type | gravity | Acid Dosage / Regeneration 100% h2so4 | 689.3424
[10 empty] | Subsurface Wash Flow | 549.6425 |  |  |  |  | Number of Reactors | 3 | Acid Dosage / Regeneration 93% h2so4 | 0.40548
[10 empty] | Subsurface Wash Time | 10 |  |  |  |  | Reactor Length | 12.9 | Caustic Dosage / Regeneration 100% NaOH | 689.3424
[10 empty] | Subsurface Wash Volume | 91.6069 |  |  |  |  | Reactor Width | 6 | Caustic Dosage / Regeneration 50% NaOH | 0.90412
[10 empty] | Backwash Flow | 549.6425 |  |  |  |  | Area | 77.4 | Backwash Temperature | 65
[10 empty] | Backwash Time | 15 |  |  |  |  | Assumed Bed depth | 2 | Preheat Temperature | 84.4444
[10 empty] | Backwash Volume | 137.4104 |  |  |  |  | Minimum Bed depth | 1.5 | Fast Backwash Flow | 5.6781
[10 empty] | Rinse Flow | 227.125 |  |  |  |  | Useable Volume (with 5% wastage) | -114.6294 | Slow Backwash Flow | 3.4069
[10 empty] | Rinse Time | 5 |  |  |  |  | Flowrate N-Units in Operation | 26 | Classify Backwash Flow | 0
[10 empty] | Rinse Volume | 18.927 |  |  |  |  | Velocity N-Units in Operation | 0.33592 | Preheat Block Flow | 29.2991
[10 empty] | Total Time | 30 |  |  |  |  | Contact Time N-Units in Operation | 267.9231 | Acid Injection Step 1 Flow | 29.5262
[10 empty] | Total Volume | 247.9444 |  |  |  |  | Cleaning Volume | 309.6 | Acid Injection Step 2 Flow | 14.536
[10 empty] | Back Wash Frequency | 0.34 |  |  |  |  | Cleaning Duration | 714.4615 | Acid Displacement / Rinse Flow | 14.3089
[16 empty] | CaCO3 Consumption/Reactor | 0.43789 | Caustic Preheat Flow | 15.6716
[16 empty] | # of Days Before filling | -15706.7194 | Caustic Injection Flow | 16.5801
[16 empty] | Volume for each Reactor | 38.7 | Caustic Displacement Flow | 15.6716
[16 empty] | Treated Water Volume /Reactor/fill | -6806.2451 | Caustic Rinse Flow | 3.8611
[16 empty] | Total Volume for all Reactors | 928.8 | Full Bed Rinse Flow | 3.8611
[16 empty] | Average refill time | -15706.7194 | Drain Down Flow | 42.6995
[16 empty] | Average Volume required /Day | -3.548 | Air Mix Flow | 13.6275
[18 empty] | Fast Fill Flow | 3.8611
[18 empty] | Final Rinse Flow | 86.9889
[18 empty] | Recycle Flow | 0
[18 empty] | Fast Backwash Time | 225
[18 empty] | Slow Backwash Time | 5
[18 empty] | Classify Backwash Time | 0
[18 empty] | Settle Time | 5
[18 empty] | Preheat Block Time | 21
[18 empty] | Acid Injection Step 1 Time | 23
[18 empty] | Acid Injection Step 2 Time | 46
[18 empty] | Acid Displacement / Rinse Time | 291
[18 empty] | Caustic Preheat Time | 21
[18 empty] | Caustic Injection Time | 60
[18 empty] | Caustic Displacement Time | 21
[18 empty] | Caustic Rinse Time | 279
[18 empty] | Full Bed Rinse Time | 4
[18 empty] | Drain Down Time | 15
[18 empty] | Air Mix Time | 15
[18 empty] | Fast Fill Time | 166
[18 empty] | Final Rinse Time | 40
[18 empty] | Recycle Time | 0
[18 empty] | Fast Backwash Volume | 21.2929
[18 empty] | Slow Backwash Volume | 0.28391
[18 empty] | Classify Backwash Volume | 0
[18 empty] | Preheat Block Volume | 10.2547
[18 empty] | Acid Injection Step 1 Volume | 11.3184
[18 empty] | Acid Injection Step 2 Volume | 11.1442
[18 empty] | Acid Displacement / Rinse Volume | 69.3979
[18 empty] | Caustic Preheat Volume | 5.4851
[18 empty] | Caustic Injection Volume | 16.5801
[18 empty] | Caustic Displacement Volume | 5.4851
[18 empty] | Caustic Rinse Volume | 17.9542
[18 empty] | Full Bed Rinse Volume | 0.25741
[18 empty] | Drain Down Volume | 10.6749
[18 empty] | Final Rinse Volume | 57.9925
[18 empty] | Regeneration Time | 856
[18 empty] | Regeneration Volume | 238.1212

## unitop_output_std
Unitop Name | A | Unitop Name | B | Unitop Name | C | Unitop Name | D | Unitop Name | E | Unitop Name | F | Unitop Name | G | Unitop Name | H | Unitop Name | I | Unitop Name | J | Unitop Name | K | Unitop Name | L | Unitop Name | M | Unitop Name | N | Unitop Type | ProductOut | Unitop Name | P | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut | Unitop Type | WasteOut
Unitop Type | Feed | Unitop Type | Feed | Unitop Type | Mixer | Unitop Type | SF | Unitop Type | Lamella | Unitop Type | MMF | Unitop Type | CF | Unitop Type | HydratedLime | Unitop Type | LimeStone | Unitop Type | IXMB | Unitop Type | RO | Unitop Type | EDI | Unitop Type | O2 | Unitop Type | CO2 | Unitop Name | O | Unitop Type | Splitter | Unitop Name | Q | Unitop Name | R | Unitop Name | S | Unitop Name | T | Unitop Name | U | Unitop Name | V
Bicarbonate | 116.6691 | Bicarbonate | 144.2517 |  |  | Maximum screen opening size | 500 micron | RW Clarifier Feed Flowrate | 90 | Diameter | 3.6576 | Total Feed Flow Rate | 87.0092 | Flow Rate | 87.0092 | Flow Rate | 87.0092 | Diameter | 0.9144 | Feed Flow Rate | 87.0092 | Product Flow Rate | 65.257 | Flow Rate | 65.2571 | Tower Diameter | 1.2192
Carbonate | 0.92015 | Carbonate | 0.14305 |  |  |  |  | Clarifier Product Flow Rate | 89.271 | Straight Shell Height | 1.6764 | No: of Filters | 24 | Temperature | 87.0092 | Temperature | 25 | Straight Shell Height | 40.2336 | Permeate Flow Rate | 65.2569 | Product Resistivity | 0 | Flux | 5.716 | Tower Height | 3.048
Co2 | 1.497 | Co2 | 15.9311 |  |  |  |  | RW Clarifier Blowdown Flowrate | 0.72905 | Vessel Design Pressure | 10.4365 | Filter DP | 0.07438 | Na | 25 | Na | 470.6782 | Vessel Design Pressure | 100.0946 | Concentrate Flow Rate | 21.7523 | Product Silica guarantee level | 0 | Inlet O2 Stage 1 | 10 | Clearwell Diameter | 1.2192
TDS | 1698.1835 | TDS | 4571.963 |  |  |  |  | Dosage | 10.0847 | Vessel Test Pressure | 13.5371 | Actual Flow per TIE | 0.90635 | K | 405.1783 | K | 8.9993 | Cation | PFC-100 H | Feed TDS | 4678.784 | Predicted Silica product | 0 | Inlet N2 Stage 1 | 17 | Clearwell Height | 4.572
[8 empty] | Hydraulic Surface Loading Rate-Based on Product Flow Rate | 0.37174 | Volume of Anthracite/Unit | 4.7125 |  |  | Ca | 8.9993 | Ca | 992.368 | Anion | PFA-400 Cl | Permeate TDS | 55.0814 | Predicted Max product sodium | 0 | Outlet O2 Stage 1 | 0.26458 | Tower + Clearwell Height | 7.62
[8 empty] | Hydraulic Surface Loading Rate-Based on Feed Flow Rate | 0.37477 | Anthracite bed depth | 0.4572 |  |  | Mg | 905.333 | Mg | 89.9928 | Inert | N/A | Concentrate TDS | 18550.8478 | Predicted Max product chloride | 0 | Outlet N2 Stage 1 | 0.23132 | Overall Height [indoors] | 7.7724
[8 empty] | Clarifier Diameter | 12.5 | Volume of Filter sand /Unit | 3.1417 |  |  | HCO3 | 89.9928 | HCO3 | 364.9345 | Cation Resin Volume / Unit | 5.3802 | Feed Pressure | 12.0225 | Predicted Max product sulfate | 0 | Outlet O2 Stage 2 | 0.007 | Overall Height [outdoors] | 8.0772
[8 empty] | Clarifier Flocculation Zone Area to total Area (%) | 20 | Filter sand bed depth | 0.3048 |  |  | CO3 | 160.4378 | CO3 | 3.8293 | Anion Resin Volume / Unit | 5.3802 | Pressure Vessels | 15 | Maximum Allowable Recovery | 0 | Outlet N2 Stage 2 | 0.0031477 | Packing Volume | 2.8317
[8 empty] | Clarifier Active Depth | 3.7 | Volume of Garnet/Unit | 2.3563 |  |  | CO2 | 0.056847 | CO2 | 3.8076 | Inert Resin Volume / Unit | 0 | Total Elements | 87 | No: of E-cell Stacks | 0 | NCG Load Stage 1 | 1.8393 | Packing Depth | 2.413
[8 empty] | Flocculation Zone HRT | 60.5352 | Garnet bed depth | 0.2286 |  |  | Cl | 49.2845 | Cl | 2070.2068 | Resin Bed Depth - Total | 20.105 |  |  | Current | 0 | H2O Load Stage 1 | 1.7741 | Design Flow | 65.2571
[8 empty] | Total HRT | 302.6759 | Volume of Greensand/Unit |  |  |  | SO4 | 2070.2068 | SO4 | 626.2903 | Cation Dosage - 100% h2so4 | 128.148 |  |  | Voltage | 0 | Volume Flow Stage 1 | 90.7807 | Normal Flow | 227.125
[8 empty] | Flocculator Cylinder Diameter | 5.5916 | Greensand bed depth |  |  |  | B | 449.9638 | B | 0 | Anion Dosage - 100% NaOH | 128.148 |  |  | DC power | 0 | Vacuum Stage 1 | 0.04945 | Design Flux | 22.9
[10 empty] | Volume of Carbon/Unit |  |  |  | Hardness | 0 | Hardness | 2851.6903 | Cation Exchange Capacity | 10 |  |  | AC power consumption | 0 | NCG Load Stage 2 | 0.12923 | Normal Flux | 79.6
[10 empty] | Carbon bed depth |  |  |  | pH | 2634.1027 | pH | 8.0252 | Anion Exchange Capacity | 10 |  |  | AC energy | 0 | H2O Load Stage 2 | 3.2417 | Clearwell Usable Capacity | 4.41
[10 empty] | Subfill Volume [to top of underdrain] | 3.8843 |  |  | Alkalinity | 6.5636 | Alkalinity | 308.5802 | Design Flow Rate | 87.0094 |  |  | Feed pressure | 0 | Volume Flow Stage 2 | 165.8779 | Clearwell Usable Depth | 3.7846
[10 empty] | Maximum Service Flow Rate per unit | 227.125 |  |  | LSI | 132.3647 | LSI | 1.9317 | Normal Flow Rate | 87.0094 |  |  | Predicted Product outlet pressure | 0 | Vacuum Stage 2 | 0.030833 | Influent CO2 ppm as CaCO3 | 4
[10 empty] | Design Service Flow Rate per unit | 227.125 |  |  | CO2 addition | 0.064371 | Remineralization Bypass | 10 | Run Time Between Regenerations at Design Flow Rate | 1440 |  |  | Feed Inlet | 65.257 | Tower Diameter | 2.4384 | Influent CO2 ppm as CO2 | 3.5
[10 empty] | Maximum Flux Rate | 9.0132 |  |  | Ca(OH)2 addition | 20 | Reactive CO2/H2SO4 | 85 | Run Time Between Regenerations at Normal Flow Rate | 1440 |  |  | Concentrate Bleed | 0 | Clearwell Diameter | 2.4384 | Effluent CO2 ppm as CaCO3 | 5
[10 empty] | Design Flux Rate | 9.0132 |  |  | NaOH addition | 10 | CO2 Stream 1A | 15 | Gross Throughput | 134072.331 |  |  | Electrode Bleed | 0 | Clearwell Volume | 23.725 | Effluent CO2 ppm as CO2 | 4.4
[10 empty] | Max Flow Rate/Media Volume | 4.0059 |  |  | CO2 Flow Rate | 9.1 | CO2 Stream 1B | 12 | Net Throughput | 125293.4955 |  |  |  |  | Straight Side Height Excluding Skirt | 15.0114 | Design [Minimum] Water Temperature | 25
[10 empty] | Design Flow Rate/Media Volume | 4.0059 |  |  | Ca(OH)2 Flow Rate | 1.7402 | NaOH | 12 | Cation Influent Load | 3893.6049 |  |  |  |  | Straight Side Height Including Skirt | 21.1074 | Recommended Fan Size | 1464.4696
[10 empty] | System Recovery | 97.4662 |  |  | NaOH Flow Rate | 0.87009 | H2SO4 | 200 | Anion Influent Load | 3926.4589 |  |  |  |  | Stage-1 Tower Packing Depth | 3.048 | Fan Size per Flow Rate | 3
[10 empty] | Draindown Flow | 0 |  |  |  |  | CaCO3 Consumption | 241.764 | Cation Exchange Capacity / Regeneration | 1900 |  |  |  |  | Stage-2 Tower Packing Depth | 3.048
[10 empty] | Draindown Time | 0 |  |  |  |  | CO2 Stream 1A Flow Rate | 0.13051 | Anion Exchange Capacity / Regeneration | 1900
[10 empty] | Draindown Volume | 0 |  |  |  |  | CO2 Stream 1B Flow Rate | 0.9397 | Design Flux Rate | 66.4978
[10 empty] | Air Scour Flow | 0 |  |  |  |  | NaOH Flow Rate | 1.0441 | Normal Flux Rate | 66.4978
[10 empty] | Air Scour Time | 0 |  |  |  |  | H2SO4 Flow Rate | 15.6617 | Design Flowrate / Resin Volume | 1.0081
[10 empty] | Refill Flow | 0 |  |  |  |  | CaCO3 Consumption Flow Rate | 18.9321 | Normal Flowrate / Resin Volume | 1.0081
[10 empty] | Refill Time | 0 |  |  |  |  | Remineralization Type | gravity | Acid Dosage / Regeneration 100% h2so4 | 689.3424
[10 empty] | Subsurface Wash Flow | 549.6425 |  |  |  |  | Number of Reactors | 3 | Acid Dosage / Regeneration 93% h2so4 | 0.40548
[10 empty] | Subsurface Wash Time | 10 |  |  |  |  | Reactor Length | 12.9 | Caustic Dosage / Regeneration 100% NaOH | 689.3424
[10 empty] | Subsurface Wash Volume | 91.6069 |  |  |  |  | Reactor Width | 6 | Caustic Dosage / Regeneration 50% NaOH | 0.90412
[10 empty] | Backwash Flow | 549.6425 |  |  |  |  | Area | 77.4 | Backwash Temperature | 65
[10 empty] | Backwash Time | 15 |  |  |  |  | Assumed Bed depth | 2 | Preheat Temperature | 84.4444
[10 empty] | Backwash Volume | 137.4104 |  |  |  |  | Minimum Bed depth | 1.5 | Fast Backwash Flow | 5.6781
[10 empty] | Rinse Flow | 227.125 |  |  |  |  | Useable Volume (with 5% wastage) | -114.6294 | Slow Backwash Flow | 3.4069
[10 empty] | Rinse Time | 5 |  |  |  |  | Flowrate N-Units in Operation | 26 | Classify Backwash Flow | 0
[10 empty] | Rinse Volume | 18.927 |  |  |  |  | Velocity N-Units in Operation | 0.33592 | Preheat Block Flow | 29.2991
[10 empty] | Total Time | 30 |  |  |  |  | Contact Time N-Units in Operation | 267.9231 | Acid Injection Step 1 Flow | 29.5262
[10 empty] | Total Volume | 247.9444 |  |  |  |  | Cleaning Volume | 309.6 | Acid Injection Step 2 Flow | 14.536
[10 empty] | Back Wash Frequency | 0.34 |  |  |  |  | Cleaning Duration | 714.4615 | Acid Displacement / Rinse Flow | 14.3089
[16 empty] | CaCO3 Consumption/Reactor | 0.43789 | Caustic Preheat Flow | 15.6716
[16 empty] | # of Days Before filling | -15706.7194 | Caustic Injection Flow | 16.5801
[16 empty] | Volume for each Reactor | 38.7 | Caustic Displacement Flow | 15.6716
[16 empty] | Treated Water Volume /Reactor/fill | -6806.2451 | Caustic Rinse Flow | 3.8611
[16 empty] | Total Volume for all Reactors | 928.8 | Full Bed Rinse Flow | 3.8611
[16 empty] | Average refill time | -15706.7194 | Drain Down Flow | 42.6995
[16 empty] | Average Volume required /Day | -3.548 | Air Mix Flow | 13.6275
[18 empty] | Fast Fill Flow | 3.8611
[18 empty] | Final Rinse Flow | 86.9889
[18 empty] | Recycle Flow | 0
[18 empty] | Fast Backwash Time | 225
[18 empty] | Slow Backwash Time | 5
[18 empty] | Classify Backwash Time | 0
[18 empty] | Settle Time | 5
[18 empty] | Preheat Block Time | 21
[18 empty] | Acid Injection Step 1 Time | 23
[18 empty] | Acid Injection Step 2 Time | 46
[18 empty] | Acid Displacement / Rinse Time | 291
[18 empty] | Caustic Preheat Time | 21
[18 empty] | Caustic Injection Time | 60
[18 empty] | Caustic Displacement Time | 21
[18 empty] | Caustic Rinse Time | 279
[18 empty] | Full Bed Rinse Time | 4
[18 empty] | Drain Down Time | 15
[18 empty] | Air Mix Time | 15
[18 empty] | Fast Fill Time | 166
[18 empty] | Final Rinse Time | 40
[18 empty] | Recycle Time | 0
[18 empty] | Fast Backwash Volume | 21.2929
[18 empty] | Slow Backwash Volume | 0.28391
[18 empty] | Classify Backwash Volume | 0
[18 empty] | Preheat Block Volume | 10.2547
[18 empty] | Acid Injection Step 1 Volume | 11.3184
[18 empty] | Acid Injection Step 2 Volume | 11.1442
[18 empty] | Acid Displacement / Rinse Volume | 69.3979
[18 empty] | Caustic Preheat Volume | 5.4851
[18 empty] | Caustic Injection Volume | 16.5801
[18 empty] | Caustic Displacement Volume | 5.4851
[18 empty] | Caustic Rinse Volume | 17.9542
[18 empty] | Full Bed Rinse Volume | 0.25741
[18 empty] | Drain Down Volume | 10.6749
[18 empty] | Final Rinse Volume | 57.9925
[18 empty] | Regeneration Time | 856
[18 empty] | Regeneration Volume | 238.1212

## MassBalance
| ac | bc | cd | de | ef | fg | gh | hi | ij | jk | kl | kp | lm | mn | no | pq | pr | ds | fu | et | lv
Flow | cum/hr | 10 | 90 | 100 | 90 | 89.271 | 87.0092 | 87.0092 | 87.0092 | 87.0092 | 87.0092 | 65.2569 | 21.7523 | 65.257 | 65.257 | 65.257 | 19.5771 | 2.1752 | 10 | 2.2619 | 0.72905 | 0
Temperature | C | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Pressure | bar | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 11.6073 | 0 | 0 | 0 | 11.6073 | 11.6073 | 1 | 1 | 1 | 0
Calcium | ppm | 100 | 1000 | 905.333 | 905.333 | 905.333 | 905.333 | 905.333 | 992.368 | 992.368 | 992.368 | 11.516 | 3934.9262 | 11.516 | 11.516 | 11.516 | 3934.9262 | 3934.9262 | 905.333 | 905.333 | 905.333 | 11.516
Magnesium | ppm | 90 | 100 | 89.9928 | 89.9928 | 89.9928 | 89.9928 | 89.9928 | 89.9928 | 89.9928 | 89.9928 | 0.9481 | 357.1269 | 0.9481 | 0.9481 | 0.9481 | 357.1269 | 357.1269 | 89.9928 | 89.9928 | 89.9928 | 0.9481
Sodium | ppm | 80 | 444.42 | 405.1783 | 405.1783 | 405.1783 | 405.1783 | 405.1783 | 412.0783 | 470.6782 | 470.6782 | 6.4687 | 1863.3082 | 6.4687 | 6.4687 | 6.4687 | 1863.3082 | 1863.3082 | 405.1783 | 405.1783 | 405.1783 | 6.4687
Potassium | ppm | 85 | 10 | 8.9993 | 8.9993 | 8.9993 | 8.9993 | 8.9993 | 8.9993 | 8.9993 | 8.9993 | 0.18142 | 35.4529 | 0.18142 | 0.18142 | 0.18142 | 35.4529 | 35.4529 | 8.9993 | 8.9993 | 8.9993 | 0.18142
Ammonia | ppm | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barium | ppm | 60 | 0.01 | 0.0089993 | 0.0089993 | 0.0089993 | 0.0089993 | 0.0089993 | 0.0089993 | 0.0089993 | 0.0089993 | 0.00010443 | 0.035684 | 0.00010443 | 0.00010443 | 0.00010443 | 0.035684 | 0.035684 | 0.0089993 | 0.0089993 | 0.0089993 | 0.00010443
Strontium | ppm | 65 | 0.1 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.0010443 | 0.35684 | 0.0010443 | 0.0010443 | 0.0010443 | 0.35684 | 0.35684 | 0.089993 | 0.089993 | 0.089993 | 0.0010443
Iron | ppm | 55 | 1 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.010443 | 3.5684 | 0.010443 | 0.010443 | 0.010443 | 3.5684 | 3.5684 | 0.89993 | 0.89993 | 0.89993 | 0.010443
Manganese | ppm | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sulfate | ppm | 200 | 500 | 449.9638 | 449.9638 | 449.9638 | 449.9638 | 449.9638 | 626.2903 | 626.2903 | 626.2903 | 6.1341 | 2486.758 | 6.1341 | 6.1341 | 6.1341 | 2486.758 | 2486.758 | 449.9638 | 449.9638 | 449.9638 | 6.1341
Chloride | ppm | 304.0973 | 2300.0071 | 2069.8439 | 2069.8439 | 2069.8439 | 2069.8439 | 2069.8439 | 2070.2068 | 2070.2068 | 2070.2068 | 22.4927 | 8213.345 | 25.0764 | 25.0764 | 25.0764 | 8213.345 | 8213.345 | 2069.8439 | 2069.8439 | 2069.8439 | 25.0764
Fluoride | ppm | 155 | 0.1 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.089993 | 0.00011061 | 0.35964 | 0.00011061 | 0.00011061 | 0.00011061 | 0.35964 | 0.35964 | 0.089993 | 0.089993 | 0.089993 | 0.00011061
Nitrate | ppm | 110 | 1 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.89993 | 0.066625 | 3.3998 | 0.066625 | 0.066625 | 0.066625 | 3.3998 | 3.3998 | 0.89993 | 0.89993 | 0.89993 | 0.066625
Bromium | ppm | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Phosphate | ppm | 25 | 5 | 4.4996 | 4.4996 | 4.4996 | 4.4996 | 4.4996 | 4.4996 | 4.4996 | 4.4996 | 0.048144 | 17.8541 | 0.048144 | 0.048144 | 0.048144 | 17.8541 | 17.8541 | 4.4996 | 4.4996 | 4.4996 | 0.048144
Boron | ppm | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Silica | ppm | 5 | 50 | 44.9964 | 44.9964 | 44.9964 | 44.9964 | 44.9964 | 44.9964 | 44.9964 | 44.9964 | 0.96292 | 177.0968 | 0.96292 | 0.96292 | 0.96292 | 177.0968 | 177.0968 | 44.9964 | 44.9964 | 44.9964 | 0.96292
H2S | ppm | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bicarbonate | ppm | 116.6691 | 144.2517 | 161.4849 | 161.4849 | 161.4849 | 161.4849 | 161.4849 | 376.4679 | 364.9345 | 364.9345 | 6.247 | 1441.9216 | 6.2682 | 6.2682 | 6.2682 | 1441.9216 | 1441.9216 | 161.4849 | 161.4849 | 161.4849 | 6.2682
Carbonate | ppm | 0.92015 | 0.14305 | 0.025253 | 0.025253 | 0.025253 | 0.025253 | 0.025253 | 0.056847 | 3.8293 | 3.8293 | 0.0040972 | 15.3378 | 0.00089715 | 0.00089715 | 0.00089715 | 15.3378 | 15.3378 | 0.025253 | 0.025253 | 0.025253 | 0.00089715
CO2 | ppm | 1.497 | 15.9311 | 72.1707 | 72.1707 | 72.1707 | 72.1707 | 72.1707 | 5.8127 | 3.8076 | 3.8076 | 3.7315 | 4.0361 | 4.386 | 4.386 | 4.386 | 4.0361 | 4.0361 | 72.1707 | 72.1707 | 72.1707 | 3.5294
TSS | ppm | 135 | 135 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
TOC | ppm | 145 | 145 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895 | 130.4895
DOC | ppm | 205 | 205 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852 | 184.4852
TKN | ppm | 95 | 95 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931 | 85.4931
COD | ppm | 165 | 165 | 148.4881 | 148.4881 | 148.4881 | 148.4881 | 148.4881 | 148.4881 | 148.4881 | 148.4881 | 22.2732 | 527.1326 | 22.2732 | 22.2732 | 22.2732 | 527.1326 | 527.1326 | 148.4881 | 148.4881 | 148.4881 | 22.2732
Turbidity | NTU | 175 | 175 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873 | 157.4873
M-Alkalinity | ppm | 225 | 120 | 308.5802 | 308.5802 | 308.5802 | 308.5802 | 308.5802 | 308.5802 | 308.5802 | 308.5802 | 5.1294 | 1207.9898 | 5.1294 | 5.1294 | 5.1294 | 1207.9898 | 1207.9898 | 308.5802 | 308.5802 | 308.5802 | 5.1294
Color | CU | 7 | 7 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995
pH | - | 8 | 7 | 8.0252 | 8.0252 | 8.0252 | 8.0252 | 8.0252 | 8.0252 | 8.0252 | 8.0252 | 6.4403 | 8.3907 | 6.4403 | 6.4403 | 6.4403 | 8.3907 | 8.3907 | 8.0252 | 8.0252 | 8.0252 | 6.4403